## Outdoor Unit
Model |  |  | 18K | 24K | 36K | 36K | 48K | 48K | 60K
|  |  | COU-V18HR1-AA01 | COU-V24HR1-A01 | COU-V36HR1-D01 | COU-V36HZR1-D01 | COU-V48HR1-D01 | COU-V48HZR1-D01 | COU-60HZVR1
Outdoor power supply |  | V/Ph/Hz | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 380~415/3/50 | 220~240/1/50 | 380~415/3/50 | 380~415/3/50
Cooling | Capacity | kW | 5.3 | 7 | 10.5 | 10.5 | 14 | 14 | 16
Heating | Capacity | kW | 5.3 | 7 | 10.5 | 10.5 | 14 | 14 | 17.6
Max. input consumption |  | W | 2200 | 3220 | 3800 | 3800 | 4900 | 4900 | 6800
Max. current |  | A | 9.6 | 14 | 16.5 | 6 | 21.3 | 7.7 | 12.8
Compressor | Model |  | KSN98D22UFZ | KSN140D21UFZ | KTM240D43UMT | KTM240D43UMT | KTM240D43UMT | KTM240D43UMT | MNB40FEQMC
| Type |  | DC/Rotary | DC/Rotary | DC/Twin-rotary | DC/Twin-rotary | DC/Twin-rotary | DC/Twin-rotary | DC/Twin-rotary
| Brand |  | GMCC | GMCC | GMCC | GMCC | GMCC | GMCC | Mitsubishi
| Frequency range | rps | 10-120 | 10-120 | 12-120 | 12-120 | 12-120 | 12-120 | 10-120
| Capacity | W | 3095 | 4370 | 7760 | 7760 | 7760 | 7760 | 12900
| Input | W | 790 | 1135 | 2055 | 2055 | 2055 | 2055 | 3960
| Refrigerant oil | ml | 370 | 440 | 620 | 620 | 620 | 620 | 1100
Outdoor fan motor | Model |  | YDK-40-6P3-AL-04 | YDK-40-6P3-AL-02 | YDK-100-6P3-2 | YDK-100-6P3-2 | YDK-100-6P3-2 | YDK-100-6P3-2 | YDK-80-6P3-1
| Brand |  | Lvzhi | Lvzhi | Sinjun | Sinjun | Sinjun | Sinjun | WEILING
| Power output | W | 40 | 40 | 100 | 100 | 100 | 100 | 80
| Speed | r/min | 890 | 890 | 850 | 850 | 850 | 850 | 780
| Insulation class |  | B | B | F | F | F | F | B
Outdoor coil | Number of rows |  | 2 | 2 | 2 | 2 | 3 | 3 | 2
| Tube pitch(a)×row pitch(b) | mm | 21×19.4 | 25×21.65 | 21×19.4 | 21×19.4 | 25×21.65 | 25×21.65 | 22×19.05
| Fin spacing | mm | 1.5 | 1.4 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Fin type |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside dia. and type | mm | 7 | 9.52 | 7 | 7 | 9.52 | 9.52 | 7.94
|  |  | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved
| Coil length×width×height | mm | 761×462×38.8 | 815×500×43.3 | 1002×756×38.8 | 1002×756×38.8 | 1003×750×64.95 | 1003×750×64.95 | 802×1280×38.1
| Number of circuits |  | 4 | 4 | 4 | 4 | 5 | 5 | 7
Outdoor air flow(High speed) |  | m3/h | 1600 | 1950 | 3900 | 3900 | 3900 | 3900 | 5500
Outdoor noise level |  | dB(A) | 51 | 53 | 57 | 57 | 58 | 58 | 58
Outdoor unit | Dimension(W×D×H) | mm | 804×304×496 | 880×345×555 | 1032×445×807 | 1032×445×807 | 1032×445×807 | 1032×445×807 | 907×400×1330
| Packing(W×D×H) | mm | 850×350×550 | 915×380×605 | 1075×495×875 | 1075×495×875 | 1075×495×875 | 1075×495×875 | 964×402×1445
| Gross/Net weight | kg | 30/28.2 | 36.7/34.2 | 64.5/60.5 | 64.5/60.5 | 70.5/66.5 | 70.6/67.3 | 106.5/98.5
Refrigerant type/quantity |  | g | R410A/1400 | R410A/1600 | R410A/2300 | R410A/2300 | R410A/3250 | R410A/3250 | R410A/3600
Throttle part |  |  | Capillary | Capillary | Capillary | Capillary | Capillary | Capillary | EXV
Design pressure |  | MPa | 4.2/1.6 | 4.2/1.6 | 4.2/1.6 | 4.2/1.6 | 4.2/1.6 | 4.2/1.6 | 4.5/1.6
Max. pressure |  | MPa | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.5
Connection wiring | Power supply |  | Indoor power supply | Indoor power supply | Outdoor power supply | Outdoor power supply | Outdoor power supply | Outdoor power supply | Outdoor power supply
| Power wiring | mm2 | 3×4 | 3×4 | 3×4 | 5×4 | 3×4 | 5×4 | 5×4
| Signal wiring | mm2 | 4×2.5 | 4×2.5 | 4×2.5 | 4×2.5 | 4×2.5 | 4×2.5 | 4×2.5
Refrigerant piping | Liquid side/Gas side | mm | Ф6.35/Ф12.7 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88
| Max. pipe length | m | 15 | 20 | 50 | 50 | 50 | 50 | 50
| Max. high drop | m | 8 | 10 | 20 | 20 | 20 | 20 | 20
Ambient temp | Cooling | °C | -15~50 | -15~50 | -15~50 | -15~50 | -15~50 | -15~50 | -15~50
| Heating | °C | -15～30 | -15～30 | -15～30 | -15～30 | -15～30 | -15～30 | -15～30

## 360 Cassette
Model |  |  | CCR-V18HR1-Q303 | CCR-V24HR1-Q303 | CCR-V36HR1-Q305 | CCR-V48HR1-Q305 | CCA-V60HR1-Q305
Indoor unit code |  |  | 821040000116 | 821040000109 | 821040000103 | 821040000102 | 821040000117
Panel code |  |  | 821055400016 | 821055400016 | 821055400016 | 821055400016 | 821055400016
Indoor power supply |  | V/Ph/Hz | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50
Cooling | Capacity | Btu/h | 18000 | 24000 | 36000 | 48000 | 60000
|  | kW | 5.3 | 7 | 10.5 | 14 | 16
| Power input | kW | 1.7 | 2.26 | 3.4 | 4.5 | 5.35
| Rated current | A | 7.8 | 10.6 | 15 | 18 | 9.6
| EER | W/W | 3.1 | 3.1 | 3.1 | 3.1 | 3
Heating | Capacity | Btu/h | 18000 | 24000 | 36000 | 48000 | 60000
|  | kW | 5.3 | 7 | 10.5 | 14 | 17.6
| Power input | kW | 1.51 | 2 | 2.8 | 4 | 4.98
| Rated current | A | 6.8 | 9.4 | 12.5 | 17.5 | 9.1
| COP | W/W | 3.5 | 3.5 | 3.4 | 3.5 | 3.21
Max. power input |  | W | 100 | 100 | 110 | 200 | 200
Max. current input |  | A | 0.4 | 0.4 | 0.5 | 0.9 | 0.9
Indoor fan motor | Model |  | YDK-35Q-8P3-1 | YDK-45Q-6P3 | YDK-75Q-6P3-1 | YDK-75Q-6P3-1 | YDK-75Q-6P3-1
| Power Output | W | 35 | 45 | 75 | 75 | 75
| Capacitor | μF | 2.5 | 3 | 5 | 5 | 5
| Speed(Hi/Me/Lo) | r/min | 480/430/380 | 850/790/600 | 740/630/530 | 740/630/530 | 740/630/530
Indoor coil | Number of rows |  | 2 | 2 | 2 | 3 | 3
| Tube pitch(a)x row pitch(b) | mm | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37
| Fin spacing | mm | 1.45 | 1.45 | 1.45 | 1.6 | 1.6
| Fin type |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside dia. and type | mm | 7 | 7 | 7 | 7 | 7
|  |  | inner grooved | inner grooved | inner grooved | inner grooved | inner grooved
| Coil length x height x width | mm | 2000×168×26.7 | 2000×168×26.7 | 2000×252×26.74 | 2000×252×40.11 | 2000×252×40.11
| Number of circuits |  | 8 | 8 | 12 | 6 | 6
Indoor air flow(High speed) |  | m3/h | 950 | 1250 | 1600 | 1900 | 1900
Indoor noise level |  | dB(A) | 35~40 | 32~42 | 45～52 | 45-52 | 45-52
Indoor unit | Dimension(W*H*D) | Body(mm) | 840×230×840 | 840×230×840 | 840×285×840 | 840×285×840 | 840×285×840
|  | Panel(mm) | 950×50×950 | 950×50×950 | 950×50×950 | 950×50×950 | 950×50×950
| Packing(W*H*D) | Body(mm) | 920×265×920 | 920×265×920 | 920×310×920 | 920×310×920 | 920×310×920
|  | Panel(mm) | 1030×100×1030 | 1030×100×1030 | 1030×100×1030 | 1030×100×1030 | 1030×100×1030
| Net/Gross weight | Body(kg) | 25/30 | 25/30 | 29/33.5 | 30.5/36 | 30.5/36
|  | Panel(kg) | 6.5/9.5 | 6.5/9.5 | 6.5/9.5 | 6.5/9.5 | 6.5/9.5
Max pressure |  | MPa | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A
Refrigerant piping | Liquid side/Gas side | mm | 6.35/12.7 | 9.52/15.88 | 9.52/15.88 | 9.52/15.88 | 9.52/15.88
Drainage pipe |  | mm | 25 | 25 | 25 | 25 | 25
Standard controller
Operation temp. |  | °C | 16～32 | 16～32 | 16～32 | 16～32 | 16～32

## 4-way Cassette (hidden)
Model |  |  | 60K
CCA-60HVR1
Indoor power supply |  | V/Ph/Hz | 220~240/1/50
Cooling | Capacity | kW | 16
| Input | W | 180
| Rated current | A | 0.8
| EER | W/W | 2.91
Heating | Capacity | kW | 17.6
| Input | W | 180
| Rated current | A | 0.8
| COP | W/W | 3.31
Energy rate |  | Cooling | C
Energy rate |  | Heating | C
Max. power input |  | W | 200
Max. current input |  | A | 0.9
Indoor fan motor | Model |  | YDK-75Q-6P3-1
| Brand |  | KAIBANG
| Power output | W | 110
| Capacitor | μF | 5
| Speed | r/min | 850/750/650
| Insulation class |  | B
Indoor coil | Number of rows |  | 3
| Tube pitch(a)xrow pitch(b) | mm | 21*13.4
| Fin spacing | mm | 1.6
| Fin type |  | Hydrophilic
| Tube outside dia. and type | mm | Ф7
Inner grooved
| Coil lengthxheightxwidth | mm | 2000*252*40.1
| Number of circuits |  | 6
Indoor air flow(High speed) |  | m3/h | 1900
Indoor noise level |  | dB(A) | 45-52
Indoor unit | Dimension(W×H×D) | Body(mm) | 840×285×840
|  | Panel(mm) | 950×50×950
| Packing(W×H×D) | Body(mm) | 920×310×920
|  | Panel(mm) | 1030×105×1030
| Net/Gross weight | Body(kg) | 29.5/35
|  | Panel(kg) | 5.4/8.0
Max pressure |  | MPa | 4.5
Refrigerant type |  |  | R410A
Refrigerant piping | Liquid side/Gas side | mm | Ф9.52/Ф15.88
Drainage pipe |  | mm | DN25
Standard controller
Operation temp |  | °C | 16～32

## New floor ceiling
Model |  |  | CUA-V18HR1-LDB | CUA-V18HR1-LDBA | CUA-V24HR1-LDBA | CUA-V36HR1-LDBB | CUA-V48HR1-LDBC | CUA-V60HR1-LDBC
Indoor unit code |  |  |  | 821039700060 | 821023700035 | 821039700053 | 821039700052 | 821025500045
Indoor power supply |  | V/Ph/Hz |  | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50
Cooling | Capacity | Btu/h |  | 18000 | 24000 | 36000 | 48000 | 60000
|  | kW |  | 5.3 | 7 | 10.5 | 14 | 16
| Power input | kW |  | 1.7 | 2.26 | 3.4 | 4.5
| Ratedcurrent | A |  | 7.8 | 10.6 | 15 | 18
| EER | W/W |  | 3.1 | 3.1 | 2.6 | 2.5
Heating | Capacity | Btu/h |  | 18000 | 24000 | 36000 | 48000
|  | kW |  | 5.3 | 7 | 10.5 | 14 | 17.6
| Power input | kW |  | 1.51 | 2 | 2.8 | 4
| Rated current | A |  | 6.8 | 9.4 | 12.5 | 17.5
| COP | W/W |  | 3.5 | 3.5 | 3.4 | 2.8
Indoor fan motor | Model |  |  | YSK110-59LD-4P17 | YSK110-59LD-4P17 | YSK110-180LD-4P2 | 2*YSK110-59LD-4P17 | 2*YSK110-59LD-4P17
| Power Output | W |  | 59 | 59 | 180 | 2*59
| Capacitor | μF |  | 3 | 3 | 5 | 2*3
| Speed(Hi/Me/Lo) | r/min |  | 1310/1139/1016 | 1310/1139/1016 | 1310/1210/1110 | 1310/1139/1016
Indoor coil | Number of rows |  |  | 3 | 3 | 3 | 3
| Tube pitch(a)x row pitch(b) | mm |  | 21×13.37 | 21x13.37 | 21×13.37 | 21*13.37
| Fin spacing | mm |  | 1.4 | 1.4 | 1.4 | 1.4
| Fin type |  |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside dia. and type | mm |  | Ф7 | Ф7 | Ф7 | Ф7
|  |  |  | inner grooved | inner grooved | inner grooved | Inner grooved
| Coil length x height x width | mm |  | 680×252*40.11 | 680×252×40.11 | 948×252×40.11 | 1300×252×40.11
| Number of circuits |  |  | 4 | 4 | 4 | 5
Indoor air flow(High speed) |  | m3/h |  | 1100 | 1200 | 1600 | 2100 | 2100
Indoor noise level |  | dB(A) |  | 49~53 | 48~52 | 51~57 | 46~55 | 46~55
Indoor unit | Dimension(W*H*D) | mm | 1050*675*235 | 1050×675×235 | 1050×675×235 | 1250×675×235 | 1670×675×235 | 1670×675×235
| Packing(W*H*D) | mm |  | 1130×765×330 | 1130×765×330 | 1380×765×325 | 1750×765×325 | 1750×765×325
| Net/Gross weight | kg |  | 26.5/31 | 26.5/31 | 32/37 | 40/46 | 40/46
Max pressure |  | MPa |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A | R410A
Refrigerant piping | Liquid side/Gas side | mm | 6.35/12.7 | 6.35/12.7 | 9.52/15.88 | 9.52/15.88 | 9.52/15.88 | 9.52/15.88
Drainage pipe |  | mm | DN25 | DN25 | DN25 | DN25 | DN25 | DN25
Standard controller |  |  | Wireless controller
Operation temp. |  | °C | 16～32 | 16～32 | 16～32 | 16～32 | 16～32

## Floor-Celing
Model |  |  | 60K
CUA-60HVR1
Indoor power supply |  | V/Ph/Hz | 220~240/1/50
Cooling | Capacity | kW | 16
| Input | W | 280
| Rated current | A | 1.15
| EER | W/W | 2.91
Heating | Capacity | kW | 17.6
| Input | W | 280
| Rated current | A | 1.15
| COP | W/W | 3.31
Energy rate |  | Cooling | C
Energy rate |  | Heating | C
Max. power input |  | W | 300
Max. current input |  | A | 1.35
Indoor fan motor | Model |  | YSK110-85LD-4P2
| Brand |  | YONGAN/KANGBAO
| Power output | W | 85
| Capacitor | μF | 5
| Speed | r/min | 1560/1430/1300
| Insulation class |  | B
Indoor coil | Number of rows |  | 4
| Tube pitch(a)xrow pitch(b) | mm | 22*19.05
| Fin spacing | mm | 1.7
| Fin type |  | Hydrophilic
| Tube outside dia. and type | mm | 7.94
Inner grooved
| Coil lengthxheightxwidth | mm | 1382/242/76.2
| Number of circuits |  | 4
Indoor air flow(High speed) |  | m3/h | 2000
Indoor noise level |  | dB(A) | 52
Indoor unit | Dimension(W×H×D) | mm | 1670×680×244
| Packing(W×H×D) | mm | 1750×770×325
| Gross/Net weight | kg | 55.5/49
Max pressure |  | MPa | 4.5
Refrigerant type |  |  | R410A
Refrigerant piping | Liquid side/Gas side | mm | Ф9.52/Ф15.88
Drainage pipe |  | mm | DN25
Standard controller
Operation temp |  | °C | 16～32

## Duct
Model |  |  | 18K | 24K | 36K | 48K | 60K | 48K | 60K
|  |  | CTA-V18HR1-F102 | CTA-V24HR1-F103 | CTB-V36HR1-F203 | CTB-V48HR1-F205 | CTB-60HVR1 | CTH-V48HR1-F305 | CTH-60HVR1
Indoor power supply |  | V/Ph/Hz | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50
Cooling | Capacity | kW | 5.3 | 7 | 10.5 | 14 | 16 | 14 | 16
| Input | kW | 1.7 | 2.26 | 3.4 | 4.5 | 340 | 4.5 | 500
| Rated current | A | 7.8 | 10.6 | 15 | 18 | 1.6 | 18 | 2.3
| EER | W/W | 3.1 | 3.1 | 2.6 | 2.5 | 2.91 | 2.5 | 2.91
Heating | Capacity | kW | 5.3 | 7 | 10.5 | 14 | 17.6 | 14 | 17.6
| Input | kW | 1.51 | 2 | 2.8 | 4 | 340 | 4 | 500
| Rated current | A | 6.8 | 9.4 | 12.5 | 17.5 | 1.6 | 17.5 | 2.3
| COP | W/W | 3.5 | 3.5 | 3.4 | 2.8 | 3.31 | 2.8 | 3.31
Indoor fan motor | Model |  | YSK100-55F-4P3/J | YSK100-68F-4P3/J | YSK120-150F-4P3H105-1 | YSK120-150F-4P3H105-2 YDK110-75F-4P3H105L-2 | YSK120-150F-4P3H105-2 YDK110-75F-4P3H105L-2 | YSK139-300F-4P3H95 | YSK139-300F-4P3H95
| Brand |  | KANGBAO | KANGBAO | XINJUN/KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
| Power output | W | 60 | 65 | 150 | 150/75 | 150/75 | 300 | 300
| Capacitor | μF | 3 | 3.5 | 5 | 6uF/4uF | 6uF/4uF | 15 | 15
| Speed | r/min | 1320/1040/700/610 | 1360/1150/920/800 | 1300/1200/1100/1060 | 1430-1320-1280-1200/1430-1370-1330-1280 | 1430-1320-1280-1200/1430-1370-1330-1280 | 1050/830/720 | 1050/830/720
| Insulation class |  | B | B | B | B | B | B | B
Indoor coil | Number of rows |  | 2 | 3 | 3 | 3 | 3 | 3 | 3
| Tube pitch(a)xrow pitch(b) | mm | 21×12.7 | 21×12.7 | 22*19.05 | 22*19.05 | 22*19.05 | 22*19.05 | 22*19.05
| Fin spacing | mm | 1.4 | 1.4 | 1.5 | 1.7 | 1.7 | 1.6 | 1.6
| Fin type |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside dia. and type | mm | Ф7 | Ф7 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94
|  |  | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved | Inner grooved
| Coil lengthxheightxwidth | mm | 715×146×27 | 915×294×38.1 | 900×308×57.15 | 1136×308×57.15 | 1136/308/57.15 | 935/330/57.15 | 935/330/57.15
| Number of circuits |  | 4 | 6 | 3 | 6 | 6 | 6 | 6
Indoor air flow(High speed) |  | m3/h | 750 | 800 | 1300 | 1900 | 2000 | 2300 | 2300
Static Pressure |  | Pa | 0-30 | 0-30 | 50-70 | 50-70 | 50-70 | 150 | 150
Indoor noise level |  | dB(A) | 28-38 | 29-39 | 33-42 | 40-52 | 40-52 | 44-52 | 44-52
Indoor unit | Dimension(W×H×D) | mm | 1010×210×467 | 1279×210×467 | 1190×260×643 | 1425×260×643 | 1425×260×643 | 1175×370×621 | 1175×370×621
| Packing(W×H×D) | mm | 1110×240×510 | 1310×240×510 | 1255×325×720 | 1490×325×720 | 1490×325×720 | 1245×445×655 | 1245×445×655
| Gross/Net weight | kg | 24.5/21.5 | 28/25 | 37/32 | 51/45 | 51/45 | 51/47 | 51/47
Max pressure |  | MPa | 4.2 | 4.2 | 4.2 | 4.2 | 4.5 | 4.2 | 4.5
Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A
Refrigerant piping | Liquid side/Gas side | mm | Ф6.35/Ф12.7 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88 | Ф9.52/Ф15.88
Drainage pipe |  | mm | DN25 | DN25 | DN25 | DN25 | DN25 | DN25 | DN25
Standard controller |  |  | Standard with wired remote controller
Operation temp |  | °C | 16～32 | 16～32 | 16～32 | 16～32 | 16～32 | 16～32 | 16～32